## AW102HUGHA
SECTION 1: |  |  | SECTION 2:
Basic Properties |  |  | Heating System Test data: I.S. EN 14825
Item Type | Heat Source |  | Test Conditions - Low (35oC)
Item Name | Heat Pump |  |  | A (88%) | B (54%) | C (35%) | D (15%) | e*(100%)
Keywords | 10kW HAIER SUPER AQUA R290 |  | Source | A-7 | A2 | A7 | A12 | A-15
Manufacturer | HAIER |  | Sink | W34 | W30 | W27 | W24 | W35
Model | AW0102HUGHA |  | Heating Capacity (kW) | 6.34 | 3.89 | 2.52 | 3.56 | 7.11
Temperature Control (Capacity Control) | Variable Outlet Temperature |  | Coefficient of Performance (kW/kW) | 3.43 | 4.88 | 6.88 | 8.83 | 2.3
Heat Source Type | Heat Pump
Heat Pump Type | Air to Water |  | Test Conditions - Medium (55oC)
Space Heating Standard | I.S. EN 14825 |  |  | A (88%) | B (54%) | C (35%) | D (15%) | e*(100%)
Water Heating Standard | I.S. EN 16147 |  | Source | A-7 | A2 | A7 | A12 | A-15
Season Space Heating Efficiency | 201 |  | Sink | W52 | W42 | W36 | W30 | W55
Water Heating efficiency | 138 |  | Heating Capacity (kW) | 5.28 | 3.24 | 2.1 | 3.22 | 5.95
TOL | -25 |  | Coefficient of Performance (kW/kW) | 2.48 | 3.62 | 5.38 | 6.66 | 1.84
WTOL | 80
SECTION 3:
Heating System Test data: I.S. EN 16147
Source of Data | Water heating Energy Efficiency | Coefficient of Performance (kW)
Water Heating Energy Efficiency ηwh (%) | 138 | Reference Hot Water Temperature |  | 52.5
Capacity of Heat Pump (kW) | 10 | Declared Load Profile |  | L
Standby Heat Loss (kWh/day) | 1.75 | Vol. Water Accounted for in Test |  | 200
P Rating for Low Temp Heat Pump | 7.2