## AW142HVGHA
SECTION 1: |  |  | SECTION 2:
Basic Properties |  |  | Heating System Test data: I.S. EN 14825
Item Type | Heat Source |  | Test Conditions - Low (35oC)
Item Name | Heat Pump |  |  | A (88%) | B (54%) | C (35%) | D (15%) | e*(100%)
Keywords | 14kW HAIER SUPER AQUA R290 |  | Source | A-7 | A2 | A7 | A12 | A-15
Manufacturer | HAIER |  | Sink | W34 | W30 | W27 | W24 | W35
Model | AW142HVGHA |  | Heating Capacity (kW) | 7.48 | 4.59 | 2.98 | 5.08 | 6.26
Temperature Control (Capacity Control) | Variable Outlet Temperature |  | Coefficient of Performance (kW/kW) | 3.12 | 4.64 | 6.75 | 8.39 | 2.17
Heat Source Type | Heat Pump
Heat Pump Type | Air to Water |  | Test Conditions - Medium (55oC)
Space Heating Standard | I.S. EN 14825 |  |  | A (88%) | B (54%) | C (35%) | D (15%) | e*(100%)
Water Heating Standard | I.S. EN 16147 |  | Source | A-7 | A2 | A7 | A12 | A-15
Season Space Heating Efficiency | 189 |  | Sink | W52 | W42 | W36 | W30 | W55
Water Heating efficiency | 140 |  | Heating Capacity (kW) | 5.98 | 3.67 | 2.38 | 4.79 | 6.74
TOL | -25 |  | Coefficient of Performance (kW/kW) | 2.36 | 3.69 | 5.46 | 6.76 | 1.64
WTOL | 80
SECTION 3:
Heating System Test data: I.S. EN 16147
Source of Data | Water heating Energy Efficiency | Coefficient of Performance (kW)
Water Heating Energy Efficiency ηwh (%) | 140 | Reference Hot Water Temperature |  | 52.5
Capacity of Heat Pump (kW) | 14 | Declared Load Profile |  | L
Standby Heat Loss (kWh/day) | 1.75 | Vol. Water Accounted for in Test |  | 200
P Rating for Low Temp Heat Pump | 8.5